## Carbon Dioxide
INCREASE / DECREASE IN CO2 IN VENTILATED BUILDINGS
The general CO2 level in an occupied ventilated room can be calculated from the document below.
The data needed for input is:-
The starting CO2 level before occupancy
| The volume of the room |  |  |  |  | ppm
| The rate of fresh air to be introduced |  |  |  |  | m³
| The time period |  |  |  |  | l/s
| The number of occupants |  |  |  |  | hours
Where a partial recirculation system is installed, only the fresh air part of the supply air should be considered.
As 400 ppm is generally accepted as a reasonable level for outdoor air, this figure has been used
as a basis for the calculations prior to room occupation. below.
If a different starting level is known, it should be entered in the grey box below.
With mechanical ventilation, it is suggested that the fresh air supply is calculated
to give a continuous level of no more than 1,000 ppm.
Constant levels of between 1,000 ppm and 2,000 ppm can give rise to drowsiness
and the feeling that the air feels “poor”.
Levels of between 2,000 ppm and 5,000 ppm will make the air feel stuffy and stagnant.
It can cause headaches, loss of attention and even nausea.
Levels above 5,000 ppm may cause serious oxygen deprivation.
If a room has constant ventilation but varying occupancy levels over a period of time,
then the rise or fall depends on that level of occupancy.
If a room is used for a long period, several calculations should be used to allow for the
interim periods when the mechanical ventilation will be changing the CO2 levels in the room.
Each period should be calculated as a separate period to gain a value.
PROJECT TITLE.
Build up of CO2 may be calculated from | [10 empty] | 132 |  | m³
Ct=(((CO + (106 * P/Q)) * (1 - e-nt)) + (Ci * e-nt) | [9 empty] | Enter volume of room
Assuming
1) That occupants exhale 0.005 l/s of CO2 per person |  |  |  |  | 0.005 |  | Fresh air quantity |  |  | 160 | l/s
2) The CO2 in the average persons breath is 35,000 to 50,000 ppm | [6 empty] | Equals |  |  | 576 | m³/hr
[7 empty] | Air change rate |  |  | 4.3636 | per hr | Gained from input data
C | concentration of CO2 ppm |  |  |  | Ci | 400 | C when starting or the calculated start figure for an ongoing period
C | concentration of CO2 ppm |  |  |  | CO | 400 | C at start normally, but see note below.
P | breath rate of CO2 from occupants l/s |  |  |  | P | 0.15 | Number of occupants |  | say | 30 | (from below)
Q | fresh air supply rate l/s |  |  |  | Q | 160 | Fresh air entered as l/s
n | room air change rate |  |  |  | n | 4.36 | Will change to rate as relevant
suffix t | after time (number of hours) |  |  |  | suffix t | 3 | Period of time. e.g. Start 9 am finish 11 am
Suffix i | initial (at time = 0) |  |  |  | suffix i | 0 | Initial start time is nil
e | 2.72 (base of natural logs) |  |  |  | e | 2.72
O | Outdoor air |  |  |  | nt | 13.08 | Air change rate times time period in hours
Note. It is generally accepted that 400 ppm is a reasonable level to assume for outdoor air. The level in the room
should normally be around this figure at the start of the day with the ventilation running and no occupants.
| If the room level is higher (local heavy industry / next to a busy road can cause this) put the known figure in the grey box. | [10 empty] | 400
| With the number of occupants listed in the yellow box below, CIBSE recommends a minimum flow rate of | [9 empty] | 240 | l/s
|  |  |  | 160 |  |  |  | 30 |  | Fill the grey & yellow areas with
|  | With fresh air of |  |  |  | l/s | and |  | occupants | relevant data.
The blue areas will be the resultant
|  |  |  | 1337.4981 |  |  |  | 3 |  | CO2 level.
|  |  | CO2 will build up to a level of |  |  | ppm | after |  | hours | The green areas may all be deleted
|  |  | (or drop in break periods etc) | [6 empty] | for the addition of your own notes.
| Calculation example |  | The room volume and fresh air rate (yellow boxes above) must be filled for table below to work.
I have filled in some times & occupancy rates for samples, Alter these as required.
| Time slot |  | Time period |  | Number of |  | Start CO2 |  | End CO2
| Start | End | Hours | Air changes | occupants | CO2 breath out
| 9:00 | 10:00 | 1 | 4.36 | 30 | 0.15 | 400 |  | 1325.5532
| 10:00 | 10:15 | 0.25 | 1.09 | 2 | 0.01 | 1325.5532 |  | 752.4729
| 10:15 | 11:15 | 1 | 4.36 | 28 | 0.14 | 752.4729 |  | 1268.3413
| 11:15 | 11:30 | 0.25 | 1.09 | 3 | 0.015 | 1268.3413 |  | 754.0011
| 11:30 | 12:30 | 1 | 4.36 | 30 | 0.15 | 754.0011 |  | 1330.0643
| 12:30 | 13:30 | 1 | 4.36 | 0 | 0 | 1330.0643 |  | 411.852
| 13:30 | 14:30 | 1 | 4.36 | 30 | 0.15 | 411.852 |  | 1325.7043
| 14:30 | 14:45 | 0.25 | 1.09 | 2 | 0.01 | 1325.7043 |  | 752.5237
| 14:45 | 15:45 | 1 | 4.36 | 40 | 0.2 | 752.5237 |  | 1638.5633
| 15:45 | 16:00 | 0.25 | 1.09 | 20 | 0.1 | 1638.5633 |  | 1231.1481
| 16:00 | 17:00 | 1 | 4.36 | 0 | 0 | 1231.1481 |  | 410.5915
| 17:00 |  |  | #VALUE! |  | 0
| 0:00 |  |  | #VALUE! |  | 0
| 0:00 |  |  | #VALUE! |  | 0
| 0:00 |  |  | #VALUE! |  | 0
| 0:00 |  |  | #VALUE! |  | 0
| 0:00 |  |  | #VALUE! |  | 0
| 0:00 |  |  | #VALUE! |  | 0
| 0:00 |  |  | #VALUE! |  | 0
| 0:00 |  |  | #VALUE! |  | 0
| 0:00 |  |  | #VALUE! |  | 0
Enter the time and occupancy data in marked area.
| Note 1. | Use 24 hr clock and correct separator for time |  |  |  | i.e. 17:30 not 17.30
| Note 2. | If you enter a high period time, you will note that the CO2 value does not increase.
This is not an error. It is as expected, as the room will reach what is called a steady-state condition.
Template prepared by Jim Lawrence of |  |  |  | B.S.C. 89 Woodlands Way, Mildenhall, Suffolk, IP28 7JA. | [5 empty] | e-mail | info@bscengineers.co.uk
|  |  |  | Telephone | 01223-926-443 |  | Telephone | 01638-714-033